ENRICH SCADA

Standard Excel Template & Dynamic Device Configuration

Implementation specification based on Bhokar - Address Details.xlsx

| Document control | Value |
| --- | --- |
| Version/date | 1.0 / 13 October 2026 |
| Source standard | Bhokar - Address Details.xlsx |
| Purpose | Define how the SCADA EXE imports the workbook and creates dynamic devices, tags and runtime configuration. |
| Audience | Product owner, PLC/Modbus engineers, developers, commissioning and O&M teams |

Governing rule: preserve the approved workbook format and make the software adapt to it.

# Contents

1. Purpose and principles

2. Actual workbook structure

3. Dynamic inverter port generation

4. Device Array groups

5. Import and validation workflow

6. Tag/address decoding rules

7. Installer and wizard

8. 24×7 runtime

9. Database/versioning

10. SCADA screens with reference images

11. Error handling and security

12. API/service contract

13. Commissioning checklist

14. Decisions requiring confirmation

Appendices: workbook examples and glossary

Screenshots in this document are supplied visual references, not proof that the UI is already implemented or connected to live data.

# 1. Purpose and Governing Principles

This document defines the SCADA configuration path using the approved workbook “Bhokar - Address Details.xlsx”. The importer must read the standard layout, validate it and convert it into normalized configuration records. Engineers should not have to re-enter the same values into a different generic template.

| Principle | Required behavior |
| --- | --- |
| Workbook is the contract | Read the approved sheet/layout; use a versioned importer profile if the layout changes. |
| Dynamic devices | Generate inverter instances from the inverter count and port rule. |
| Separate Device Array | Treat WMS, Trafo, TVM, Annunciator and future groups as distinct logical devices/groups. |
| No hard-coded tags | Names, addresses, function codes and counts come from the workbook or approved decoding profile. |
| Validate before activation | Import → validate → preview → test → publish. |
| Independent runtime | Acquisition and sync continue after browser closure. |
| Auditability | Record source workbook name/hash, import user/time, warnings and published version. |

Initial scope is monitoring, historian, alarms and reports. PLC writes, remote switching and safety/control commands are outside this specification unless separately reviewed.

# 2. Actual Workbook Structure

The uploaded workbook contains sheet “Venus 4.0MWp” with 140 rows and 11 columns. The upper rows hold site/inverter settings; the left table is the inverter parameter map; the right table is the Device Array parameter map.

| Source field | Value visible in workbook | Interpretation |
| --- | --- | --- |
| Customer | Venus Wire Industries Pvt.Ltd. | Customer metadata |
| Site | Bhokar, MH. | Site identity |
| Capacity | 2.65 MW AC, 4 MWp DC | Store AC/DC capacity separately where possible |
| Inverter Make / Count | Hopewind / 08 Nos | Manufacturer and number of generated inverter instances |
| Function Code | FC3 / Holding | Modbus operation/register profile; confirm normalization |
| Inverter endpoint | IP 192.168.X.X; base port 501 | Shared IP and sequential inverter ports described in workbook |
| Inverter Start / Data Count | 1 / 124 | Metadata requiring agreed address/count semantics |
| Device Array endpoint | IP Other Paramerts; port None | Separate endpoint for additional device group |
| Device Array Start / Data Count | None / None | Separate array-section configuration |
| Inverter table | Sr. No. / Parameters / Address | Parameter-to-address mapping |
| Device Array table | Sr. No. / Parameters / Address / Device Name | Additional equipment mapping grouped by Device Name |

| Area | Current workbook cells (observed) | Use |
| --- | --- | --- |
| Site summary | B2:D6 | Customer, site, capacity, make/count and function metadata |
| Inverter endpoint | B9:D12 | IP, base port, start address and data count |
| Device Array endpoint | G9:J12 | IP, port, start address and data count |
| Inverter mapping | B:D from row 15 onward | Serial number, parameter, address |
| Device Array mapping | G:J from row 15 onward | Serial number, parameter, address, Device Name |

The current layout is the import contract. If the team changes row/column positions, the importer should detect the mismatch and request a new importer profile rather than silently misread values.

# 3. Dynamic Inverter Port Generation

The workbook example describes 8 inverters on the same configured IP, using ports 501–508, and the Device Array endpoint on port 509. The planned 10-inverter example uses ports 501–510 and Device Array port 511.

8-inverter workbook example: INV-01 → configured IP : 501 INV-02 → configured IP : 502 ... INV-08 → configured IP : 508 Device Array → configured IP : 509 10-inverter planned example: INV-01 → configured IP : 501 ... INV-10 → configured IP : 510 Device Array → configured IP : 511

| Field | Rule |
| --- | --- |
| Inverter count | Parse “08 Nos” as integer 8; require positive integer. |
| Base port | Read from workbook; validate 1–65535. |
| Port formula | inverter_port(i) = base_port + (i - 1), where i starts at 1. |
| Shared IP | Apply the same IP to each endpoint only when the gateway design confirms that pattern. |
| Device Array port | If workbook explicitly provides it, use that value and compare it with the calculated next port. If not, use configured rule base_port + inverter_count only after approval. |
| Port collision | Validate duplicates and range; show generated list before publishing. |
| Connectivity | Test each port; a generated port is valid only if the gateway/device actually exposes/routes it. |

Do not hard-code the Device Array port to 509 or 511. In the current example it is explicitly 509; in the future 10-inverter scenario the calculated port is 511. Explicit workbook input should take precedence, with a warning if it conflicts with the configured sequential rule.

# 4. Device Array Groups and Relay/Annunciator Tags

In this workbook, “Device Array” means the right-hand additional-equipment parameter section, not automatically a mathematical array. Group rows by Device Name. A Device Name entered on the first row applies to following rows until the next nonblank Device Name, unless the workbook owner specifies otherwise.

| Device Name | Examples from workbook | SCADA treatment |
| --- | --- | --- |
| WMS | GTI, cumulative/total GTI, GHI, shadow irradiation, rain, ambient/module temperature, humidity, wind speed/direction | Weather/irradiance asset group |
| Trafo | WTI 01/02, OTI 01/02 | Transformer temperature group |
| TVM | R/Y/B voltage/current, neutral current, active/reactive/apparent power, frequency, PF, export/import | Metering group; confirm naming and meaning |
| Annunciator | Ann Status: W-1 through W-24 | Status/relay/alarm points; bit semantics require engineering map |
| Future group | Any new Device Name value | Create configurable group after validation; no code change should be required |

Do not clone inverter tags into the Device Array section.

Use the Device Array endpoint by default; allow per-group endpoint overrides only if the standard is extended to support them.

Preserve parameter names and addresses, while mapping them to stable Universal Tag Codes separately.

Allow shared equipment to map to one or more plants without duplicate physical acquisition.

Relay/annunciator entries must specify register type, bit offset/mask or raw-value enum, normal state, alarm state and severity before alarm behavior is enabled.

# 5. Import, Validation and Preview Workflow

Select workbook ↓ Validate workbook/sheet profile and required fields Parse site metadata + inverter map + Device Array groups ↓ Normalize count, IP, ports, function/register type and addresses Generate inverter instances + group Device Array parameters ↓ Validate address/count/ports/tags/data decoding Preview generated devices, ports, tags and warnings ↓ Test connections and representative reads Save DRAFT → approve/publish immutable configuration version ↓ Acquisition service loads ACTIVE version

| Validation | Examples | Action |
| --- | --- | --- |
| Workbook profile | Missing sheet or required fields | Reject import; show exact issue |
| Inverter count | Cannot parse or zero/negative | Block publish |
| Port generation | Port outside 1–65535 or collision | Block publish |
| Endpoint test | One port unreachable | Show result per device; apply agreed partial-commissioning policy |
| Address map | Duplicate or invalid address | Warn/block based on explicit overlap rules |
| Function code | Unknown/contradictory register type | Require engineering confirmation |
| Data Count | Meaning unclear or exceeds request limit | Do not assume it is Modbus quantity; block activation until defined |
| Device grouping | Address row has no resolved Device Name | Warn and require mapping review |
| Decoder metadata | No data type/scale/unit/byte order | Use approved model profile or require engineering input |
| Config diff | Existing tags/addresses changed | Preview affected devices before publish |

## 5.1 Configuration states

DRAFT → VALIDATING → VALIDATED → PUBLISHED → ACTIVE ↘ FAILED A failed draft never replaces the active version. Rollback is auditable.

## 5.2 Data Count caution

The workbook shows Data Count 124, while the address list contains entries extending beyond the first 124 parameter rows depending on how the column is interpreted. The engineering team must define whether Data Count means Modbus registers per request, tags/parameters in the map, or a vendor-specific setting. The software must not blindly use 124 as a read length.

# 6. Tag, Address and Decoder Rules

The workbook visibly supplies parameter labels and addresses, but not all decoding details. Data type, signedness, register type, byte/word order, scale, offset, unit, bit location and polling interval must come from an approved manufacturer/model profile or explicit engineering input.

| Layer | Purpose | Example |
| --- | --- | --- |
| Display parameter | Original label in workbook | Active Power |
| Universal Tag Code | Stable company standard semantic identifier | AC_POWER |
| Template mapping | Device-specific function/address/decoder | FC3 + address 4001 + approved type/scale |
| Asset tag instance | Concrete device-specific tag | INV-01 / AC_POWER |
| Live/history value | Typed value, quality and timestamp | 125.6 kW, GOOD, timestamp |

Preserve the original workbook address value; separately store its addressing convention.

Confirm whether 4001 means a protocol offset, a 4xxxx reference, or a vendor-specific address. Never silently subtract one or rewrite it.

Normalize FC3/Holding only after engineering confirms how the workbook uses these labels.

Use contiguous block reads only when the device supports the range and the mapping defines child offsets correctly.

Validate data type/register count, request limits, overlapping addresses and invalid/sentinel values.

Create stable Tag Codes through a reviewed dictionary; preserve original display names for traceability.

Do not infer relay alarm polarity or state meanings from labels alone.

engineering_value = raw_value × scale_factor + offset

# 7. Installer and First-Run Wizard

| Step | Screen/action | Output |
| --- | --- | --- |
| 1 | Install prerequisites and application services | One customer-facing installer completed |
| 2 | Create administrator | Secure initial account |
| 3 | Import standard workbook | Draft configuration + validation report |
| 4 | Review site and inverter count | Confirmed site and device count |
| 5 | Review endpoint generation | IP and generated inverter ports preview |
| 6 | Review Device Array groups | WMS/Trafo/TVM/Annunciator grouping and endpoint |
| 7 | Review decoder profile | Function, address, type, scale, units and polling |
| 8 | Test connection/read | Per-device results and raw/decoded values |
| 9 | Central server and retention | Central sync and local retention settings |
| 10 | Validate and publish | Active immutable configuration version |
| 11 | Runtime health | Service status, live data, sync backlog |

SCADA-Setup.exe installs/registers: React/TypeScript frontend FastAPI service Modbus acquisition service Central sync service Retention service Optional watchdog/health service PostgreSQL as a managed prerequisite or installer-managed component

Suggested Windows services: EnrichSCADA_API, EnrichSCADA_Acquisition, EnrichSCADA_Sync, EnrichSCADA_Retention and optional EnrichSCADA_Watchdog. The browser is not responsible for polling PLCs.

# 8. Runtime and 24×7 Behavior

Windows boot → PostgreSQL ready → API starts → Acquisition loads ACTIVE config snapshot → connect to generated inverter endpoints and Device Array endpoint → poll/decode/scale/quality-check → write current values + historian + alarms + sync outbox → sync worker uploads batches to central API → retention service manages local history

| Scenario | Expected behavior |
| --- | --- |
| Browser closed | Acquisition, local database, alarms, sync and retention continue. |
| Internet unavailable | Local reads/history continue; outbox remains pending; sync resumes later. |
| One inverter offline | That endpoint shows communication failure/stale quality; other devices continue. |
| Service crash | Windows recovery restarts service; health log records outage. |
| Bad import | Draft rejected; active version unchanged. |
| Count changed | Preview generated endpoints/tags and validate port conflicts before publish. |
| Template update | Show a diff; affected assets migrate only after explicit approval. |

Never display failed communication as a valid zero. Keep last known value with its timestamp and STALE/COMMUNICATION_FAILURE quality.

# 9. Database Model and Versioning

| Table/group | Purpose |
| --- | --- |
| sites / plants | Site and plant identity/capacity/timezone |
| assets | Generated inverters and logical Device Array assets/groups |
| asset_plant_mappings | Map shared WMS/Trafo/TVM/Annunciator/PLC to one or more plants |
| communication_configurations | Protocol, IP/port or serial settings, timeout/retry and Unit ID |
| tag_definitions | Universal Tag Codes, names, units, category and approval state |
| device_templates | Versioned manufacturer/model register map |
| template_tag_mappings | Workbook parameter/address and decoder metadata |
| asset_tag_instances | Resolved tags per generated device, with effective address/index |
| register_blocks | Contiguous read ranges and child offsets |
| current_values | Latest value, quality and timestamp per tag instance |
| historical_values | Time-series records, partitioned by time |
| device_status | Connection state, last success/failure and response time |
| alarm_rules / alarm_events | Alarm definitions and lifecycle |
| sync_queue | Durable outbox with unique event ID and retry state |
| configuration_versions / changes | Immutable snapshots and old/new differences |
| service_heartbeat / audit_logs / users | Runtime health, traceability and access control |

Store the imported workbook name, format version, content hash, importer user and timestamp.

Store a normalized snapshot; do not depend on a mutable Excel file at runtime.

Published versions are immutable. Corrections create a new version.

Acquisition reports which configuration version it loaded.

Failed validation/reload leaves the last known-good version active.

Use PostgreSQL time partitioning for high-volume history; retention should not delete unsynced outbox events.

# 10. SCADA Screens and Visual References

Use the agreed dark theme: background #132238, panels #1E2D3D, header #0D1B2A, white primary text, #D6DCE5 secondary text, #29B6F6 accent, #00C853 healthy, #FFC107 warning, #FF5252 alarm, #FFCA28 solar generation, #42A5F5 grid flow, #26A69A export and #EF5350 import. Every live value should show unit and freshness/quality.

## 10.1 Dashboard / Portfolio

Reference: dashboard

Portfolio KPIs, plant status, live generation, energy, trend, alarm summary and last-data timestamp. Filters follow selected site/plant.

## 10.2 AC Single-Line Diagram

Reference: AC SLD

Configured electrical topology with live power flow, equipment state and alarm/communication indicators. Topology must be configurable per plant.

## 10.3 Trend / History

Reference: trend

Tag selection, custom time range, multi-series charts, zoom/cursor and export. Use historian queries and downsampling.

## 10.4 Inverter Data

Reference: inverter data

Display dynamically generated inverter instances, connection status, values, quality, last read and device drill-down.

## 10.5 String Data

Reference: string data

Display string/MPPT values only when supported by the selected inverter map; do not invent unsupported values.

## 10.6 Architecture / Topology

Reference: architecture

Site, plants, inverter groups and shared WMS/other assets. Shared assets may map to multiple plants without duplicate acquisition.

## 10.7 Alarms

Reference: alarms

Active/acknowledged/cleared events with severity, time, asset, tag, value, message and acknowledgement identity.

## 10.8 Reports / Analytics

Reference: reports

Daily, MTD, YTD and custom reports. Document formula, timezone, counter reset and missing-data handling.

## 10.9 WMS

Reference: WMS

Show supported irradiance, temperature, humidity, wind and rain tags from the Device Array mapping.

## 10.10 Required configuration screens

| Screen | Required fields/actions |
| --- | --- |
| Workbook Import | File selection, detected sheet/profile, validation results and source hash |
| Inverter Port Preview | IP, count, base port, generated ports and conflicts |
| Device Array Manager | Device Name, endpoint, parameters, addresses, enable/disable and preview |
| Universal Tag Dictionary | Add/review/approve stable Tag Codes, names, units and categories |
| Template/Address Map | Function/register type, address, data count, type, byte/word order, scale, unit and test read |
| Publish Configuration | Diff, validation summary, confirmation and rollback |
| System Health | Service heartbeats, loaded version, device states, last read, sync backlog, DB/disk and retention |

# 11. Error Handling, Security, Backup and Updates

| Condition | Required behavior |
| --- | --- |
| Workbook layout mismatch | Explain changed/missing fields; never guess silently. |
| Invalid count/port | Block publish and identify the offending field. |
| Unreachable endpoint | Show per-device result and apply agreed commissioning policy. |
| Unknown function/address/count | Require engineering correction before activation. |
| Unknown data type/scaling | Require approved decoding profile; never assume a type. |
| Database unavailable | Report unhealthy and retry; no false persistence success. |
| Central API unavailable | Retain pending outbox and retry with backoff. |
| Disk nearly full | Raise critical health alarm and follow documented safe degradation. |

Use least-privilege Windows service accounts and PostgreSQL roles.

Enforce RBAC server-side; protect secrets and validate TLS.

Audit workbook imports, publishing/rollback, user changes and alarm acknowledgement.

Keep rotating structured logs; never log credentials/tokens.

Default local historian retention is 365 days; partition by time at scale.

Do not delete unsynced sync events solely because historian data is old.

Back up configuration/database and test restore; use versioned DB migrations for upgrades.

# 12. API and Service Contract

| Area | Suggested endpoint | Purpose |
| --- | --- | --- |
| Workbook import | POST /api/v1/config/import-workbook | Parse workbook into draft; return warnings and preview ID |
| Import preview | GET /api/v1/config/imports/{id}/preview | Show endpoints, Device Array groups and generated tags |
| Connection test | POST /api/v1/assets/{id}/test-connection | Test endpoint |
| Tag test | POST /api/v1/assets/{id}/test-read | Return raw registers, decoded value, quality and timestamp |
| Validation | POST /api/v1/config/versions/{id}/validate | Validate draft |
| Publish | POST /api/v1/config/versions/{id}/publish | Activate immutable version |
| Rollback | POST /api/v1/config/rollback | Reactivate known-good version |
| Live/history | GET /api/v1/current-values; GET /api/v1/history; WebSocket /ws/live | Dashboard and trends |
| Health/sync | GET /api/v1/system/health; /services; /sync/status | Runtime monitoring |

These are proposed contracts for implementation, not claims that the APIs already exist.

# 13. Commissioning and Acceptance Checklist

| Test | Acceptance criteria |
| --- | --- |
| Workbook import | Approved workbook imports without manual restructuring. |
| Site metadata | Customer, site, capacity, make/count and function are parsed and shown for confirmation. |
| Port generation | 8 devices with base 501 produce 501–508; 10 produce 501–510; Device Array follows explicit/configured rule. |
| IP/port reality | Each generated endpoint is tested; port pattern matches actual gateway routing. |
| Device Array grouping | WMS, Trafo, TVM and Annunciator rows are grouped correctly. |
| Address preservation | Workbook values are not silently shifted or transformed. |
| Data Count | Meaning is confirmed and protocol/device limits validated. |
| Decoder validation | Type, byte/word order, scaling and units are tested against known values. |
| Version safety | Failed drafts cannot replace active configuration; rollback is audited. |
| 24×7 runtime | Closing browser does not stop acquisition; reboot restarts services. |
| Offline sync | Local data persists during central outage and later sync is idempotent. |
| Retention/backup | Retention protects unsynced queue; database restore is tested. |
| Screen acceptance | Supplied screen references guide implementation; all live values are API-driven. |

# 14. Decisions Requiring Engineering Confirmation

| Decision | Why | Required action |
| --- | --- | --- |
| Data Count=124 | Could mean read count, tag count or vendor-specific setting | Document precise meaning per profile before runtime use |
| Address convention | 4001 may be offset/reference/vendor notation | Store convention and test read; do not auto-shift |
| FC3/Holding | Function code and register type need exact normalization | Approve internal mapping |
| Data types and scaling | Workbook does not specify all decoder metadata | Create approved model-specific decoding profile |
| Device Array port | Example is 509 for 8 inverters; planned 511 for 10 | Explicit workbook value takes precedence; calculate only if policy says so |
| Device Name carry-down | Group labels may only appear at first row | Approve carry-forward rule until next nonblank group label |
| Relay/annunciator states | Labels do not define bit polarity or alarm meaning | Document bit/enum values, normal/alarm state and severity |
| Shared IP | Ports only work if gateway routes/listens there | Test every endpoint |

# Appendix A. Workbook-Derived Parameter Examples

| Inverter parameter | Address shown | Engineering note |
| --- | --- | --- |
| Active Power | 4001 | Decoder and unit must be confirmed |
| DC Power | 4002 | Confirm address convention and type |
| Reactive Power | 4003 | Confirm type and scale |
| Today Generation | 4004 | Confirm unit/reset behavior |
| Total Generation | 4005 | Confirm counter type/rollover |
| Power Factor | 4006 | Confirm range and scaling |
| Grid Frequency | 4007 | Confirm unit/scaling |
| Internal Temp. | 4009 | Confirm unit/scaling |
| Status | 4010 | Define raw-value enum |
| R/Y/B Phase Voltage | 4014–4016 | Check contiguous block feasibility |
| String Current 01–32 | 4026–4057 | Repeated parameter group in source |
| MPPT Voltage 01–12 | 4058–4069 | Repeated parameter group in source |
| MPPT Current 01–12 | 4070–4081 | Repeated parameter group in source |

| Device Array group | Examples |
| --- | --- |
| WMS | GTI, cumulative/total GTI, GHI, shadow irradiation, rain, ambient/module temperature, humidity, wind |
| Trafo | WTI 01/02, OTI 01/02 |
| TVM | Phase voltage/current, neutral current, active/reactive/apparent power, frequency, PF, import/export |
| Annunciator | Ann Status: W-1 through W-24 |

Names and addresses above are transcribed from the workbook for documentation only; they do not define the correct raw data decoding.

# Appendix B. Final Implementation Rules

Use the approved workbook as the source configuration contract.

Generate inverter ports dynamically from count/base port; use explicit Device Array port when supplied.

Treat Device Array as grouped additional equipment, not automatically as a mathematical array.

Do not guess function codes, address conventions, data types, scaling or Data Count semantics.

Preview and test endpoints/tags before publishing.

Keep active configuration immutable and preserve rollback.

Continue local acquisition when UI or Internet is unavailable.

Use supplied SCADA screen images as visual guidance; bind production UI to live APIs.